AC1-2WT  Digital Stat set up

Recalibration instructions:

- Press the  and  simultaneously, hold down for 5 seconds

- “SCL” will be displayed

- Press the &to select the parameter to be displayed or modified,  Set to 2c to give Centigrade readout.

- Now press the  button, the display shows parameter value.

- Press and hold the  ,Whilst holding pressing the  &to select the desired value. ( see list below)

- When you let go the , the newly add value is stored and the displayed shows the next parameter.

- When complete, Press the  button for 30 seconds.

- The parameters are now set.

- Now reset the unit will show the current probe temperature.

To set the working temperature:-

1. Press L1, (the    arrow), and let go. The led L1 blinks, the display shows SPL for  1 second, then the current set point value.

2. Press the & to select the temperature required.

3. Press   for 10 seconds to store the information.

4. the parameters  and recommended values are as follows;

Parameter List:-

SCL	=	2

SPL	=	5

SPH	=	40

1SP	=	temperature set point e.g 28 ( deg C)

1CH	=	HY

1CH	=	HEA

1HY	=	1

1T0	=	0

1T1	=	0

1PF	=	OFF

OAU	=	NON

AMT	=	NON

SB	=	NO

INP	=	ST1

OS1	=	0

TLD	=	5

SIM	=	0

ADR	=	30